## Reported Electrical Incidents and Occurrences

First Quarter – January to March, 2002

Date & 	Program	Location		Accident Description

MIS ID #

Incidents - Fatal:

There were no fatal injuries of an electrical nature reported to the Ministry for the first quarter of 2002.

Incidents - Critical:

January 16th	Construction	London		Electrician was installing electrical conduit when he contacted

1009648						an energized wire.  Worker fell backwards and hit head.

Suffered broken shoulder and had stitches in head.

January 24th	Construction	Toronto		Electrician was working on an electrical panel when an arc

1009936 & 1010260 (same event)			occurred.  Flash caused burns to right hand, right forearm, and

to forehead and top of head.

January 24th	Construction	London		Electrician contacted 347 volts, received burns to both hands.

1009937						No information given as to nature of work being done.

February 16th	Industrial	Almonte		Worker was changing a fluorescent tube when he contacted the

1010605						exposed contact pins within the fixture.  Worker was thrown

back from the area of the fixture and was reported to have lost

consciousness.  Fixture operated at 120 volts.

March 27th	Industrial	North York	Worker received burns to hands and face while trying to

1012966						connect an electrical cord inside a disconnect box.  Box

voltage was 600 volts.

Incidents - Non-Critical:

January 7th	Construction	Thunder Bay	Worker contacted 110 volts as a result of backfeed and

1001409						improper wiring by a previous contractor.

January 9th	Construction	Burlington	Worker received an electrical shock while doing non-electrical

1009699						work in the false ceiling.  He knocked the MARRETTE off an

electrical connection for a light fixture.

January 11th	Construction	Brantford	Worker was using a reciprocating saw when he cut into an

1009547						electrical conduit.  Worker received a 110 volt shock, and fell

from the step ladder he was using.  Worker was cutting

through a plaster and lath ceiling at the time.

January 17th	Construction	Carleton Place	Electrician was working on a 600 volt panel, panel was still

1011291						live.  Worker received an electrical shock, taken to hospital.

Returned to work the same day.

January 22nd	Construction	Toronto		Worker was drilling into a pipe, with water still in the pipe.

1010579						Worker received an electrical shock, was sent to hospital.

January 25th	Industrial	Oshawa		Worker received an electrical shock.  Treated at hospital then

1009990						released.  No information given as to work being done.

January 25th	Industrial	 Toronto		Worker was testing fuses in an electrical box.  Arc occurred,

1010117						worker received flash burns to both hands.  No information

given on type of tester being used.

February 1st	Industrial	Caledonia	Linesman contacted 4800 volt powerline while making repairs

1012618						on the line.  No information given on injuries received.

February 7th	Construction	Toronto		Worker received an electrical shock.  No other information

1010622						given.

February 10th	Industrial	Guelph		Worker was using a meter to check a capacitor bank in a

1011917						switchroom.  Meter was a process calibration meter, rated for

300 volts maximum, capacitor bank operated at 600 volts.

Flash from arc caused burns to face and hands.  Meter was

clearly labeled with voltage rating.

February 11th	Construction	Brampton	While working in proximity to an old cable, a worker

1010546						inadvertently contacted the cable.  Cable was still energized,

worker received a shock from an exposed wire from the cable.

February 13th	Industrial	Etobicoke	As worker was turning on a power box, it exploded.  Worker

1010541						received burns to face, neck and arms.  No information given

on type of switch the worker was operating.

February 14th	Industrial	Richmond Hill	Worker received a shock from an electrical outlet.  No burns

1010564						but worker was shook up by incident.  No information given as

to whether the receptacle or the cord and plug were faulty.

February 20th	Construction	Sarnia		Supervisor received a shock from 480 volt equipment.

1012104						Supervisor was reported as “tinkering” with the equipment at

the time of the contact.

February 26th	Industrial	Nepean		Worker was changing a bulb in a vending machine when

1023599						contact was made with an exposed energized wire.

March 8th	Industrial	Concord		Worker received an electrical shock and 2nd degree burns to

1011246						both hands.  No information given as to work being done at

time of incident.

March 12th 	Industrial	Burlington	Worker received an electrical shock from the switch on the

1020486						machine that the worker was operating.

March 21st	Construction	Mississauga	As splitter cover door was opened, an explosion occurred.

1015496						Worker received burns to face and right hand.  No information

given on what may have initiated the arc.

Reportable Occurrences - Powerline Contacts:

January 14th	Industrial	Township of 	Tractor-trailer contacted an overhead line as the truck moved

1010594				Cavan		forwards.  No other details given.

January 14th	Construction	Greely		Power shovel contacted a buried 4800 volt power line.

1011295						No locates done.

February 5th	Construction	Thunder Bay	Worker was cutting through a cement floor with a saw, cut

1001464						through an electrical cable.

February 6th	Construction	Toronto		Electrical contact with 27 kV line.  No other details given.

1011222

February 6th	Construction	Collingwood	Electrical contact made as crew was installing sewer and water

1011898				Township	lines.  No other details given.

February 10th	Construction	St. Catherines	Backhoe contacted a buried hydro line.

1010771						Line was rated for 11, 240 volts.

February 12th	Construction	Mississauga	Bobcat with an auger attachment hit an energized cable.

1012017

March 29th	Construction	Toronto		Sheathing of buried cable was ruptured.  No other details

1015737						given.

# DATA SUMMARY - First Quarter

Fatals:		Critical:	Non-criticals:		Powerline	Electrical

Contacts:	Equipment:

2002		    0		      5		        18			        8		        0

2001		    1		      7		        21			      11		        1

2000		    1		    12		        10			      16		        3

1999		    1		      7		        16			      13		        1

1998		    1		      9		          7			        9		        0

Information taken from MIS database, July 25, 2002

Produced by:	Michael Reiser

Engineer

PSS – Kitchener District

Phone:	(519) 883-5682

FAX:	(519) 883-5694

E-Mail:	mike.reiser@mol.gov.on.ca