## Selected Electrical Incidents and Occurrences

First Quarter - January to March, 2003

Date & 	Program	Location	Accident Description

MIS ID #

Accidents - Fatal:

There were no fatal injuries of an electrical nature reported to the Ministry of Labour for the first quarter of 2003.

Accidents - Critical:

January 28th	Industrial	Toronto		Worker received an electrical shock and 3rd degree burns to

1035712						his right hand and arm while shutting off power on an

electrical panel.  No details given of the specific equipment

involved.

February 21st	Industrial	Mississauga	Worker touched an energized wire while working on an

1036850						electrical fixture.  Connection had not been properly capped

during construction.  Worker fell off ladder, broke right elbow.

February 28th	Construction	Toronto		Worker contacted a 347 volt conductor, lost consciousness.

1037012

March 6th	Industrial	St. Catherines	Worker made contact with 13.8 kV electrical equipment while

1037176						inside a vault, receiving burns to 60% of his body.  Event

description stated that the worker was not authorized to be in

the vault, did not give information on work he was doing.

March 19th	Industrial	Listowel		Worker made electrical contact, receiving burns to forearm.

1037622						No information given on work being done at the time.

Accidents - Non-Critical:

January 6th	Construction	Kitchener	Workers were getting shocks from a portable heater.

1034854

January 22nd	Construction	Toronto		Worker received an electrical shock, and fell from a ladder.

1035766						No other details of event given.

January 31st	Industrial	Toronto		As a worker was checking a rail electrical bond, a loose end

1035812						of the bond contacted the live power rail.  Worker received

temporary blurred vision from the flash.

February 3rd	Construction	Cambridge	Electrician was connecting the ground wire inside a disconnect

1036651						switch.  Switch handle was OFF, left phase terminal on line

side of switch was exposed at the side.  Electrician’s hand

brushed against phase terminal.

February 11th	Construction	Nanticoke	Worker was making test measurements, received an electrical

1036460						shock from 110 volts.

February 12th	Industrial	Guelph		Electrician was working on a transformer, screwdriver touched

1036392						energized wires.  Electrician received 3rd degree burns on right

hand.

February 17th	Industrial	Tecumseh	Worker received a shock while working on a Wheelabrator.

1036625						Worker taken to hospital and released.

February 19th	Industrial	Brampton	Worker received an electrical shock from a power box, was

1036759						“thrown” down the stairs.  No details of the work being done.

March 11th	Construction	Cobourg		Worker contacted 600 volts, received burns to one arm.

1037354						No details given of work being done at the time.

March 13th	Construction	Cambridge	Worker contacted a 480 volt busbar inside a crane rail.

1037534						Worker received a shock and felt tingling in his arm, there

were no visible signs of injury.  Worker was not aware that the

crane rail contained electrical conductors.

March 14th	Industrial	Ottawa		Worker was changing a bulb in an EXIT sign.  Made contact,

1037488						received burn to finger and tingling in arm.

March 19th	Industrial	Fort Erie	Two non-workers climbed a transmission tower, one person

1037623						made contact with one of the conductors.  The resulting arc

caused his clothes to catch on fire.  Other person put out the

fire, both people were able to climb back down on their own.

March 29th	Industrial	Cambridge	Worker received an electrical shock while turning on a light

1037897						switch.

March 31st	Industrial	Richmond Hill	A commercial steam iron exploded.  Worker received steam

1037920						burns, electrical shock, and hit his head on the ground.

Reportable Incidents - Powerline Contacts:

January 2nd	Construction	Tiverton		Event classified as an electrical contact with no injuries.

1034937						No other details of event given.

January 6th	Construction	Toronto		While auguring, contacted 13.8 kV buried cable.

1034884

January 8th	Construction	Mississauga	Excavator contacted power line.

1034949

January 9th	Construction	Toronto		Debris was knocked onto power lines.

1034963

January 13th	Mining		Timmins		Raised box of dump truck snagged communications cable.

1035267						Cable caused two poles to break.

February 13th	Construction	Toronto		Blade of concrete cutting saw contacted 120 volt power line.

1036743

February 17th	Construction	Thunder Bay	Boom of boom truck contacted 115 kV power line.

1036676

February 20th	Mining		Sudbury		A Caterpillar 966 Loader backed into a guy wire for a

1036820						69 kV power line.  Pole broke, power knocked off.

February 26th	Construction	Thunder Bay	Boom of backhoe contacted neutral of power line.

1037006						Line bounced, contacted one of the power conductors.

February 27th	Construction	Guelph		Contact made with secondary of hydro line, no other details

1037244						of event given.

February 28th	Construction	Woodbridge	Boom of excavator pulled down a hydro wire.

1037021

March 3rd	Construction	Nanticoke	Event classified as an electrical occurrence.  No other

1037091						details of event given.

March 4th	Construction	Brampton	Electrical contact made, no other details of event given.

1037124

March 5th	Construction	Toronto		Power line contact made.  Telephone sagged and contacted

1037281						the power line.  No details given of equipment involved.

March 7th	Construction	Kitchener	Contractor was doing trenching, contacted the primary cable.

1037242

March 7th	Mining		Levack		Raised mast of a diamond drill contacted one phase of an

1037264						overhead line.  Drill was being towed up a slope when the

towing attachment failed.  The drill slid down the slope and

contacted the power line.

March 12th	Construction	Burlington	Crane contacted overhead power line.

1037379

March 12th	Industrial	St. Joseph’s 	Tree contractor dropped a branch onto Bell cable, causing the

1037402				Island		power cables to sway.  Conductors touched, power kicked off.

March 20th	Industrial	Simcoe		Tree trimming contractor dropped a tree onto the services for

1037651						two residences.  Services were torn down.

March 24th	Construction	Dryden		Blast caused blasting mats to contact power line.

1037730

March 28th	Construction	Toronto		Power line contact made, no other details given.

1037953

March 30th	Industrial	London		While tree trimming, a branch was dropped onto a 2400 V

1037928						power line, breaking it.

# DATA SUMMARY - First Quarter

Fatals:		Critical:	Non-criticals:		Powerline	Electrical

Contacts:	Equipment:

2003		     0		     5		          14			        22		          0

2002		     0		     5		          18			          8		          0

2001		     1		     7		          21			        11		          1

2000		     1		   12		          10			        16		          3

1999		     1		     7		          16			        13		          1

1998		     1		     9		            7			          9		          0

Information taken from MIS database,  April 29, 2003

Produced by:	Michael Reiser

Engineer

PSS – Kitchener District

Phone:	(519) 883-5682

FAX:	(519) 883-5694

E-Mail:	mike.reiser@mol.gov.on.ca