## Selected Electrical Accidents and Incidents

First Quarter - January to March, 2001

Date & 	Program	Location	Accident Description

MIS ID #

Accidents - Fatal:

March 12th 	Industrial	Woolwich	Worker electrocuted while working on electrical wires running

79373				Township	in a conduit.  Wiring energized at 600 volts.  The insulative

covering for a wire had been damaged during the installation

of the wires in the conduit, exposing the copper conductor for

a short distance.  The damage was not visible from in front of

the junction box.  While the worker reached around the bundle

of wires with his hand, his fingers contacted the bare copper.

Accidents - Critical:

January 4th	Industrial	Brampton	Worker passed out after receiving an electrical contact.

77387						No other information given.

January 5th	Industrial	Nanticoke	Worker doing potential tests on a 600 volt breaker using a

77450						potential checking device.  Arc occurred at the breaker, worker

received severe burns to hands and face.  Potential checking

device was of a type authorized by the utility but was not

CSA approved.

January 23rd	Construction	Toronto		Utility worker was stripping a splice in a manhole, contacted

78129 & 78129					13.8 kV.  Suffered burns to left hand and wrist, and to right

foot.  Cable was not labelled properly, spiking not done.

February 6th	Industrial	Toronto		Worker was working on electrical boxes, received burns to

78468						hands and face.

February 14th	Industrial	Grand Bend	Worker contacted electricity from a 4000 volt switchgear.

78749						No information given as to the nature of injuries suffered.

February 27th	Industrial	Toronto		Worker was doing work on an electrical contact box when it

79024						exploded.  Worker received burns to hands, arms, face and

neck.

March 21st 	Industrial	Strathroy	Workers were using a boom truck near 2400 volt power line.

1000458						Contact made, one worker lost consciousness.

Accidents - Non-Critical:

January 2nd	Industrial	Scarborough	Worker connecting 600 volt wires, did not shut off the power.

77634						Wire touched metal, arc occurred.  Worker burned on face and

left arm.

January 4th	Industrial	St. Thomas	Two workers installing a meter, meter dropped on a live wire.

77892						Flash occurred, one worker received burns.

January 8th	Industrial	Tilbury		Worker suffered light burns on nose, right hand and neck from

78443						a fire caused by an electrical hazard.  No details given as to

nature of the hazard or what work was being done.

January 18th	Industrial	Kitchener	Worker was testing a power supply, received a 120 volt shock.

78321						Had numbness in hand, dizziness and nausea.

January 18th	Industrial	Brantford	Electrician was fishing a wire, received a 110 volt shock.

78461						Worker was knocked off the ladder he was on.

January 22nd	Industrial	London		Worker received a shock when he touched a breaker after

79283						a line blew.  No other details of accident given.

January 23rd	Industrial	Bolton		Worker was trying to plug an arc welder into a power source.

77976						Received a shock, felt tingling in arms and chest area.

January 25th	Construction	Toronto		Worker received an electrical shock while installing drywall.

79248						No information given on source of electrical shock.

January 29th	Construction	Sault Ste Marie	Worker removing BX cable from a junction box.  As he pulled

78484						on the BX, the junction box came loose, worker contacted an

energized 120 volt conductor.  Worker felt shock across his

chest, fell off the ladder.

January 30th	Construction	North York	Worker doing electrical work from a ladder.  Hand grazed a

78495						live wire, worker received burns to left hand, fell off ladder.

February 8th	Construction	St. Catherines	Worker received a shock from a 120 volt source.  No other

79159						details given.

February 13th	Industrial	Ottawa		Worker received an electrical contact.  No other information

79909						given as to injuries or nature of work being done.

February 15th	Construction	Kincardine	Worker was installing a new cable when his elbow contacted

79846						347 volts from another cable in the area.  Cable was energized

and uncapped.

February 16th	Construction	Cambridge	Worker made electrical contract with 600 volts.  No

78899						information given as to work being done at time of accident.

March 4th	Industrial	Alliston		Worker received an electrical shock when he touched an

79243						elevating platform.

March 12th	Industrial	Hamilton	Worker opened a panel to inspect it, electrical short occurred.

80636						Worker received burns to hand and wrist.

March 16th	Mining		Crean Hill	Workers trying to place a transformer draw down shelf back

79551						into position.  After experiencing difficulties, they stopped and

were looking over the situation when a flash occurred.  Both

workers received flash burns to their faces.

March 22nd	Construction	Toronto		While installing a light, an insulating cap fell off a connection.

79975						The worker’s hand touched the connection, received a shock.

March 26th	Construction	Strathroy	Two workers using a boom truck, boom contacted 2400 volts.

1000748						Worker on ground fell over and dislocated his shoulder.

March 27th	Construction	Mississauga	Worker received an electrical shock while using on a ladder.

79842						Worker fell off the ladder, no information given as to work

being done at the time.

March 28th	Construction	London		Worker received a shock from 4160 volts.  No other accident

1000875						information given.

Reportable Incidents - Powerline Contacts:

January 12th	Construction	Toronto		Directional boring machine was pulling pipe, contacted

78850						three 4 kV power lines.

January 23rd	Construction	Brampton	Backhoe cut into a 27 kV cable while digging.

77923

January 25th	Construction	Brampton	Crane contacted overhead power lines, power out to homes in

78142						the area.

January 30th	Industrial	Oakville		Power line contact.  No other details given.

79035

January 31st	Industrial	Wawa		Boom on a logging truck contacted the neutral of a 7200 V

78298						power line.  The neutral contacted two phases of a 115 kV

power line, seven generators at the power plant taken

off-line.

February 13th	Construction	Hamilton	Backhoe hit house service line while digging for gas line

79242						installation to house.  No locates done.

February 26th	Industrial	Highway #11,	Box of dump truck hit power line.

79193				Atikokan

February 27th	Construction	Toronto		Concrete pump truck contacted a power line, blew a tire off

79556						the truck.  Foil insulation detached from the truck’s pipe line

in the wind and contacted the overhead line.

March 9th	Construction	Waterloo	Dump truck hit power line while box was still elevated.

79993

March 9th	Construction	Nanticoke	Worker was using concrete saw, cut through a 110 volt cable.

80056

March 23rd	Construction	Ajax		Drilling rig hit 13.8kV conductor and neutral line.  No injuries.

80562

Reportable Incidents - Electrical Equipment:

March 12th	Construction	Stoney Creek	Possible electrical contact at an industrial establishment.

80647						Power out, employer refused to allow the utility to enter the

electrical room.

# DATA SUMMARY - First Quarter

Fatals:		Critical:	Non-criticals:		Powerline	Electrical

Contacts:	Equipment:

2001		     1		       7		        21			      11		        1

2000		     1		     12		        10			      16		        3

1999		     1		       7		        16			      13		        1

1998		     1		       9		          7			        9		        0

Information taken from MIS database, September 12, 2001

Produced by:	Michael Reiser

Engineer

PSS – Kitchener District

Phone:	(519) 883-5682

FAX:	(519) 883-5694

E-Mail:	mike.reiser@mol.gov.on.ca