# Electrical Incidents and Occurrences

Annual Summary for 2003

Table 1: - Number of Events by Quarter per Year:

Category	  1st Quarter	  2nd Quarter	  3rd Quarter	  4th Quarter		Total

Fatals:

2003		 0		 3		 5		 0		   8

2002		 0		 1		 1		 0		   2

2001		 1		 1		 2		 5		   9

2000		 1		 2		 2		 2		   7

1999		 1		 2		 3		 2		   8

1998		 1		 2		 5		 1		   9

#### Total –Fatals:		 4		11		18		10		  43

Criticals:

2003		  5		  7		   6		 7		 25

2002		  5		  9		 10		 4		 28

2001		  7		13		   5		 9		 34

2000		12		  5		   5		 8		 30

1999		  7		  9		 11		 7		 34

1998		  9		  4		 13		 8		 34

Total – Criticals:	              45		47		 50		43		185

Non-criticals:

2003		14		25		 24		19		 82

2002		18		17		 34		15		 84

2001		21		12		 25		28		 86

2000		10		22		 26		15		 73

1999		16		22		 24		21		 83

1998		  7		17		 13		15		 52

Total – Non-criticals:	86	             115	              146	             113		460

Power line contacts:

2003		22		39		 50		37		148

2002		  8		28		 59		37		132

2001		11		32	 	 44		33		120

2000		16		34		 42		30		122

1999		13		32		 40		30		115

1998		  9		30		 40		29		108

#### Total – PLNC’s:		79	             195		275	             196		745

Electrical Equipment:

2003		  0		  0		   4		 0		    4

2002		  0		  1		   0		 1		    2

2001		  1		  2		   1		 1		    5

2000		  3		  1		   0		 1		    5

1999		  1		  0		   0		 1		    2

1998		  0		  0		   2		 2		    4

Total – Equipment:	 5		 4		   7		 6		   22

Total Events:

2003		 41		 74		  89		63		267

2002		 31		 56		104		57		248

2001		 41		 60		  77		76		254

2000		 42		 64		  75		56		237

1999		 38		 65		  78		61		242

1998		 26		 53		  73		55		207

Grand Total:	          219	           372		496	          368	         1 455

Commentary for Table 1 (above)

In the above table, if a person (not necessarily a worker) was injured during the event, it would be counted as a fatal, critical, or non-critical depending on the nature of the injury.  Events are placed in the category of occurrences for power line contacts or electrical equipment only if a person was not injured.

Commentary for Table 2 (following):

The headings are defined as follows;

- Meters, if the direct cause of the event involved the malfunction of a meter, the event would be counted here.  It would be considered as a malfunction of the meter even if the cause were the worker using it on the wrong function or scale.

- Equipment being worked on while still live, if the worker was working directly on the piece of electrical equipment.  If a worker caused the fault with his test leads, the accident would be placed here, and not in the Meters column, as the meter itself did not cause the event.

- Close proximity to live equipment, if the worker did not intend to do anything with the electrical equipment, but inadvertently made contact.  Roofing and siding workers losing control of their metal ladders would be placed here.

- Faulty equipment, if the worker was using the equipment properly, but it had a fault, which caused the event.  Faulty power drills would go here.

Table 2 - Detailed Summary of Injury Events by Specified Cause:

Category	Meters		Equipment being worked	Close proximity	Faulty

on while still live		to live equipment	equipment

Fatals:

2003		    0			    3				  4			   1

2002		    0			    2				  0			   0

2001		    0			    4				  4			   1

2000		    0			    3				  3			   1

1999		    0			    1				  7			   0

1998		    0			    4				  4			   1

Totals		   0			  17				22			  4

Criticals:

2003		    2			  11				   8			   4

2002		    0			  17				   9			   2

2001		    3			  14				   9			   8

2000		    0			  20				   6			   4

1999		    1			  19				 12			   2

1998		    4			  19				 10			   1

Totals		 10			100				54			21

Non-criticals:

2003		    0			   44				 14			  24

2002		    4			   38				 16			  26

2001		    4			   43				 12			  27

2000		    1			   35				 17			  20

1999		    1			   40				 15			  27

1998		    2			   27				 11			  12

Totals		  12			227				85			136

Overall:

2003		    2			   58				 26			 29

2002		    4			   57				 25			 28

2001		    7			   61				 25			 36

2000		    1			   58				 26			 25

1999		    2			   60				 34			 29

1998		    6			   50				 25			 14

### Grand Total	 22			344			           161		           161

Thoughts to ponder from Table 2;

Of the 43 fatalities recorded over the past six years, 22 occurred while workers were doing work in close proximity to exposed electrical equipment.  Of these 22 deaths, 9 occurred as workers lost control of aluminum ladders while moving them or placing them in position.  The ladder contacted one or more phases of an overhead line, and as the electrical current flowed through the ladder to ground, some also went through the worker holding the ladder.  With only about 100 milliamperes required to cause ventricular fibrillation in the human body, not much of the available fault current would have to go through the worker to cause death.

In looking at the total number of events resulting in worker injuries or death, half involved workers doing work directly on electrical equipment while it was still energized.  While the Construction, Industrial and Mining Programs all allow work to be done on or near to exposed electrical equipment while it is still energized, it is only for limited circumstances in which the work is not practical to be done any other way.  Trouble-shooting using a meter or voltage tester would be an example of this.  In all other circumstances, the power must be turned off before the work is started, and while the work is being done on or near to the electrical equipment.

Table 3 - Detailed Summary of Power Line Contacts:

Overhead Lines					Buried Cables

Crane	Dumptruck	Tree felling 	Other			Digging	Other

2003		  16	      19		       9		   63			    35		   6

2002		  16	      20		       4		   50			    36		   6

2001		  16	      22		       5		   43			    27		   7

2000		  15	      10		       3		   59			    32		   3

1999		  11	      26		       2		   48			    27		   1

1998		  10	      17		       8		   39			    27		   7

Totals:	  84	     114		      31		  302			   184		  30

Commentary:

Unless the event description gave clear information on a specific category, the event would be placed in the Overhead Lines – Other category.  With the brief descriptions that are many times phoned into the Ministry of Labour offices, this category collects many of the events by default.

Produced by:	Mike Reiser, P. Eng.,

Engineer,

PSS-Kitchener District

Phone:	(519) 883-5682

FAX:	(519) 883-5694

E-Mail:	mike.reiser@mol.gov.on.ca

Date of issue:	January 13, 2004